## CCGT
Egy gáz/gőz kombinált ciklusú erőmű (CCGT) az alábbi ábra szerinti kapcsolásban üzemel. A gázturbinás blokk 82% hatásfokú kompresszora 1 bar nyomású, 15 °C hőmérsékletű és 500 kg/s tömegáramú levegőt szív be, majd azt 12 bar nyomásra komprimálja. A levegő adiabatikus kitevője 1,4, izobár fajhője 1004,5 J/(kg×K), állandónak tekinthető. A füstgáz adiabatikus kitevője 1,33, izobár fajhője megegyezik a levegőjével és állandónak tekinthető. Az égőtérből távozó füstgáz hőmérséklete 1450 K. A füstgáz a 92% hatásfokú turbinában környezeti nyomásig expandál. A tüzelőanyag földgáz, melynek fűtőértéke 40 MJ/kg, entalpiája elhanyagolható. A hőhasznosító kazánban a füstgázt 125 °C-ra hűtik le. A hőhasznosító kazánba 70 kg tápvíz lép be másodpercenként. A minimális hőfokrés a víz és a füstgáz között 15 °C. A gőzturbina hatásfoka 80 %. A tápszivattyú munkája adiabatikus és reverzibilis. – Számítsa ki a kombinált ciklusú erőmű eredő hatásfokát! – Ábrázolja léptékhelyesen a hőhasznosító kazánban végbemenő folyamatokat T-Q diagramban!
Adatok
Kompresszor |  |  | Gázturbina
p1 | 1 | bar | T3 | 1450 | K | t_fg [°C] | t_gőz [°C] | Q [MW] | Régió
p2 | 12 | bar | cp_fg | 1004.5 | J/kg/K
T1 | 288.15 | K | h_GT | 0.92 | -
m_air | 500 | kg/s | k_fg | 1.33 | -
cp_air | 1004.5 | J/kg/K | Hü | 40 | MJ/kg
h_komp | 0.82 | -
k_air | 1.4 | -
Számolás
Kompresszor |  |  | HH kazán
T2 |  | K | Q_HH |  | MW
T2* |  | K | m_tv | 70 | kg/s
P_komp |  | MW
Gázturbina |  |  | p_sat_HH |  | bar
T4 |  | K | Vízhevítő
T4* |  | K | Q_fg |  | MW
m_ü |  | kg/s | Q_tv |  | MW
m_fg |  | kg/s | T_fg_be |  | K
P_GT |  | MW | T_fg_ki | 398.15 | K
Q_be |  | MW | Elgőzölögtető
h_GT |  | - | Q_E |  | MW
Gőzturbina |  |  | T_sat |  | K
h_ST | 0.8 | - | ΔT_PP |  | K
h_S4 |  | kJ/kg | h_L |  | kJ/kg
h_S4* |  | kJ/kg | h_V |  | kJ/kg
p_S4 | 0.05 | bar | T_fg_be |  | K
P_ST |  | MW | T_fg_ki |  | K
Tápszivattyú |  |  | Túlhevítő
s_S1 |  | kJ/kg/K | Q_TH |  | MW
h_S1 |  | kJ/kg | T_fg_be |  | K
h_S2 |  | kJ/kg | T_fg_ki |  | K
T_S2 |  | °C | T_S3 |  | K
P_sziv |  | kW | h_S3 |  | kJ/kg
Körfolyamat |  |  | s_S3 |  | kJ/kg/K
P_össz |  | MW
eta_össz |  | -

## CCGT_p_valt
ÁBRÁZOLÁS
Egy gáz/gőz kombinált ciklusú erőmű (CCGT) az alábbi ábra szerinti kapcsolásban üzemel. A gázturbinás blokk 82% hatásfokú kompresszora 1 bar nyomású, 15 °C hőmérsékletű és 500 kg/s tömegáramú levegőt szív be, majd azt 12 bar nyomásra komprimálja. A levegő adiabatikus kitevője 1,4, izobár fajhője 1004,5 J/(kg×K), állandónak tekinthető. A füstgáz adiabatikus kitevője 1,33, izobár fajhője 1004,5 J/(kg×K), állandónak tekinthető. Az égőtérből távozó füstgáz hőmérséklete 1450 K. A füstgáz a 92% hatásfokú turbinában környezeti nyomásig expandál. A tüzelőanyag földgáz, melynek fűtőértéke 40 MJ/kg, entalpiája elhanyagolható. A hőhasznosító kazánban a minimális hőfokrés a víz/gőz és a füstgáz között 15 °C. A gőzturbina hatásfoka 80%. A tápszivattyú munkája adiabatikus és reverzibilis. – Számítsa ki a kombinált ciklusú erőmű eredő hatásfokát és ábrázolja diagramban a gőzfejlesztési nyomás függvényében! – Ábrázolja léptékhelyesen a hőhasznosító kazánban végbemenő folyamatokat T-Q diagramban! | [22 empty] | OPTIMÁLIS NYOMÁS |  |  |  | NAGYNYOMÁS
[23 empty] | Q | tfg | tgőz | Régió | Q | t_gőz | Régió
Adatok
Kompresszor |  |  | Gázturbina
p1 | 1 | bar | T3 | 1450 | K
p2 | 12 | bar | cp,fg | 1004.5 | J/(kg×K)
T1 | 288.15 | K | hGT | 0.92 | -
mair | 500 | kg/s | kfg | 1.33 | -
cp,air | 1004.5 | J/(kg×K) | Hü | 40 | MJ/kg
hK | 0.82 | -
kair | 1.4 | -
Számolás
Kompresszor |  |  | Gázurbina |  |  | Gőzciklus |  |  | Hőhasznosító
T2 | 586.0789 | K | T4 | 782.7106 | K | hST | 0.8 | - | Δtpp | 15 | °C
T2* | 651.478 | K | T4* | 836.0938 | K | pS1 | 0.05 | bar
PK | 182.4815 | MW | mü | 10.0264 | kg/s | sS1 | #VALUE! | kJ/kg/K
|  |  | mfg | 510.0264 | kg/s | hS1 | #VALUE! | kJ/kg
|  |  | PGT | 314.5174 | MW | tS3 | 547.9438 | °C
|  |  | Qbe | 401.0577 | MW
|  |  | hGT | 32.9219 | %
psat | tsat | tpp | hS2 | hL | hV | hS3 | mtv | QVH | QELG | QTH | QHH | T5 | sS3 | hS4 | hS4* | PST | Psziv | PCCGT | hCCGT | hSTEAM | Tbe | xS4*
[bar] | [°C] | [°C] | [kJ/kg] | [kJ/kg] | [kJ/kg] | [kJ/kg] | [kg/s] | [MW] | [MW] | [MW] | [MW] | [°C] | [kJ/kg/K] | [kJ/kg/K] | [kJ/kg] | [MW] | [kW] | [MW] | [%] | [%] | [°C] | [%]
2
5
10
15
20
25
30
35
40
45
50
55
60
65
70
75
80
85
90
95
100
105
110
115
120
125
130
135
140
145
150
155
160
165
170
175
180

## Properties (hidden)
X Steam Tables
Excel macros, IF-97 Steam tables. |  | The excel scripts are stored inside this workbook. A complete list of functions for use is available on the "Calling functions" worksheet
By: Magnus Holmgren |  | The steam tables are free and provided as is. We take no responsibilities for any errors in the code or damage thereby.
www.x-eng.com |  | OBS: This workbook uses macros. Set security options in Tools:Macro:Security… to enable macros.
Saturation properties given temperature |  |  | Saturation properties given pressure
Temperature | 100 | °C | Pressure | 12.57 | bar a
Saturation pressure | #VALUE! | bar a | Saturation temperature | #VALUE! | °C
Liquid |  |  | Liquid
Enthalpy | #VALUE! | kJ/kg | Enthalpy | #VALUE! | kJ/kg
Density | #VALUE! | kg/m3 | Density | #VALUE! | kg/m3
Entropy | #VALUE! | kJ/kgK | Entropy | #VALUE! | kJ/kgK
Vapour |  |  | Vapour
Vapour enthalpy | #VALUE! | kJ/kg | Vapour enthalpy | #VALUE! | kJ/kg
Vapour density | #VALUE! | kg/m3 | Vapour density | #VALUE! | kg/m3
Vapour Entropy | #VALUE! | kJ/kgK | vapour Entropy | #VALUE! | kJ/kgK
Evaporation energy | #VALUE! | kJ/kg | Evaporation energy | #VALUE! | kJ/kg
Properties given pressure and temperature |  |  | Properties given pressure and enthalpy
Pressure | 1 | bar a | Pressure | 12.57 | bar a
Temperature | 20 | °C | Enthalpy | 2788 | kJ/kg
Enthalpy | #VALUE! | kJ/kg | Temperature | #VALUE! | °C
Density | #VALUE! | kg/m3 | Density | #VALUE! | kg/m3
Entropy | #VALUE! | kJ/kgK | Entropy | #VALUE! | kJ/kgK
Vapour fraction | #VALUE! | % | Vapour fraction | #VALUE! | %
IF97 Region | #VALUE! |  | IF97 Region | #VALUE!
Phase | #VALUE! |  | Phase | #VALUE!
Isobaric heat capacity | #VALUE! | kJ/kg | Isobaric heat capacity | #VALUE! | kJ/kg
Speed of sound | #VALUE! | m/s | Speed of sound | #VALUE! | m/s

## Functions (hidden)
X Steam Tables |  |  | v2.6 | http://www.x-eng.com
Steam tables by Magnus Holmgren according to IAPWS IF-97
The excel scripts are stored inside this workbook. (No extra files are needed. Start from a copy of this workbook. This page can be removed)
For error-reporting, feedback, other units etc. contact: |  |  |  |  | magnus@x-eng.com
The steam tables are free and provided as is. We take no responsibilities for any errors in the code or damage thereby.
OBS: This workbook uses macros. Set security options in Tools:Macro:Security… to enable macros.
Temperature
Tsat_p | 1 | bar |  |  | #VALUE! | °C | Saturation temperature
T_ph | 1 | bar | 100 | kJ/kg | #VALUE! | °C | Temperture as a function of pressure and enthalpy
T_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | °C | Temperture as a function of pressure and entropy
T_hs | 100 | kJ/kg | 0.2 | kJ/(kg K) | #VALUE! | °C | Temperture as a function of enthalpy and entropy
Pressure
psat_T | 100 | °C |  |  | #VALUE! | bar | Saturation pressure
p_hs | 84 | kJ/kg | 0.296 | kJ/(kg K) | #VALUE! | bar | Pressure as a function of h and s.
p_hrho | 2000 | kJ/kg | 5 | kg/m3 | #VALUE! | bar | Pressure as a function of h and rho (density). Very unaccurate for solid water region since it's almost incompressible!
Enthalpy
hV_p | 1 | bar |  |  | #VALUE! | kJ/kg | Saturated vapour enthalpy
hL_p | 1 | bar |  |  | #VALUE! | kJ/kg | Saturated liquid enthalpy
hV_T | 100 | °C |  |  | #VALUE! | kJ/kg | Saturated vapour enthalpy
hL_T | 100 | °C |  |  | #VALUE! | kJ/kg | Saturated liquid enthalpy
h_pT | 1 | bar | 20 | °C | #VALUE! | kJ/kg | Entalpy as a function of pressure and temperature.
h_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | kJ/kg | Entalpy as a function of pressure and entropy.
h_px | 1 | bar | 0.5 |  | #VALUE! | kJ/kg | Entalpy as a function of pressure and vapour fraction
h_Tx | 100 | °C | 0.5 |  | #VALUE! | kJ/kg | Entalpy as a function of temperature and vapour fraction
h_prho | 1 | bar | 2 | kg/m3 | #VALUE! | kJ/kg | Entalpy as a function of pressure and density. Observe for low temperatures (liquid) this equation has 2 solutions. (Not valid!!)
Specific volume
vV_p | 1 | bar |  |  | #VALUE! | m3/kg | Saturated vapour volume
vL_p | 1 | bar |  |  | #VALUE! | m3/kg | Saturated liquid volume
vV_T | 100 | °C |  |  | #VALUE! | m3/kg | Saturated vapour volume
vL_T | 100 | °C |  |  | #VALUE! | m3/kg | Saturated liquid volume
v_pT | 1 | bar | 100 | °C | #VALUE! | m3/kg | Specific volume as a function of pressure and temperature.
v_ph | 1 | bar | 1000 | kJ/kg | #VALUE! | m3/kg | Specific volume as a function of pressure and enthalpy
v_ps | 1 | bar | 5 | kJ/(kg K) | #VALUE! | m3/kg | Specific volume as a function of pressure and entropy.
Density
rhoV_p | 1 | bar |  |  | #VALUE! | kg/m3 | Saturated vapour density
rhoL_p | 1 | bar |  |  | #VALUE! | kg/m3 | Saturated liquid density
rhoV_T | 100 | °C |  |  | #VALUE! | kg/m3 | Saturated vapour density
rhoL_T | 100 | °C |  |  | #VALUE! | kg/m3 | Saturated liquid density
rho_pT | 1 | bar | 100 | °C | #VALUE! | kg/m3 | Density as a function of pressure and temperature.
rho_ph | 1 | bar | 1000 | kJ/kg | #VALUE! | kg/m3 | Density as a function of pressure and enthalpy
rho_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | kg/m3 | Density as a function of pressure and entropy.
Specific entropy
sV_p | 0.006117 | bar |  |  | #VALUE! | kJ/(kg K) | Saturated vapour entropy
sL_p | 0.0061171 | bar |  |  | #VALUE! | kJ/(kg K) | Saturated liquid entropy
sV_T | 0.0001 | °C |  |  | #VALUE! | kJ/(kg K) | Saturated vapour entropy
sL_T | 100 | °C |  |  | #VALUE! | kJ/(kg K) | Saturated liquid entropy
s_pT | 1 | bar | 20 | °C | #VALUE! | kJ/(kg K) | Specific entropy as a function of pressure and temperature (Returns saturated vapour entalpy if mixture.)
s_ph | 1 | bar | #VALUE! | kJ/kg | #VALUE! | kJ/(kg K) | Specific entropy as a function of pressure and enthalpy
Specific internal energy
uV_p | 1 | bar |  |  | #VALUE! | kJ/kg | Saturated vapour internal energy
uL_p | 1 | bar |  |  | #VALUE! | kJ/kg | Saturated liquid internal energy
uV_T | 100 | °C |  |  | #VALUE! | kJ/kg | Saturated vapour internal energy
uL_T | 100 | °C |  |  | #VALUE! | kJ/kg | Saturated liquid internal energy
u_pT | 1 | bar | 100 | °C | #VALUE! | kJ/kg | Specific internal energy as a function of pressure and temperature.
u_ph | 1 | bar | 1000 | kJ/kg | #VALUE! | kJ/kg | Specific internal energy as a function of pressure and enthalpy
u_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | kJ/kg | Specific internal energy as a function of pressure and entropy.
Specific isobaric heat capacity
CpV_p | 1 | bar |  |  | #VALUE! | kJ/(kg°C) | Saturated vapour heat capacity
CpL_p | 1 | bar |  |  | #VALUE! | kJ/(kg°C) | Saturated liquid heat capacity
CpV_T | 100 | °C |  |  | #VALUE! | kJ/(kg°C) | Saturated vapour heat capacity
CpL_T | 100 | °C |  |  | #VALUE! | kJ/(kg°C) | Saturated liquid heat capacity
Cp_pT | 1 | bar | 100 | °C | #VALUE! | kJ/(kg°C) | Specific isobaric heat capacity as a function of pressure and temperature.
Cp_ph | 1 | bar | 200 | kJ/kg | #VALUE! | kJ/(kg°C) | Specific isobaric heat capacity as a function of pressure and enthalpy
Cp_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | kJ/(kg°C) | Specific isobaric heat capacity as a function of pressure and entropy.
Specific isochoric heat capacity
CvV_p | 1 | bar |  |  | #VALUE! | kJ/(kg°C) | Saturated vapour isochoric heat capacity
CvL_p | 1 | bar |  |  | #VALUE! | kJ/(kg°C) | Saturated liquid isochoric heat capacity
CvV_T | 100 | °C |  |  | #VALUE! | kJ/(kg°C) | Saturated vapour isochoric heat capacity
CvL_T | 100 | °C |  |  | #VALUE! | kJ/(kg°C) | Saturated liquid isochoric heat capacity
Cv_pT | 1 | bar | 100 | °C | #VALUE! | kJ/(kg°C) | Specific isochoric heat capacity as a function of pressure and temperature.
Cv_ph | 1 | bar | 200 | kJ/kg | #VALUE! | kJ/(kg°C) | Specific isochoric heat capacity as a function of pressure and enthalpy
Cv_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | kJ/(kg°C) | Specific isochoric heat capacity as a function of pressure and entropy.
Speed of sound
wV_p | 1 | bar |  |  | #VALUE! | m/s | Saturated vapour speed of sound
wL_p | 1 | bar |  |  | #VALUE! | m/s | Saturated liquid speed of sound
wV_T | 100 | °C |  |  | #VALUE! | m/s | Saturated vapour speed of sound
wL_T | 100 | °C |  |  | #VALUE! | m/s | Saturated liquid speed of sound
w_pT | 1 | bar | 100 | °C | #VALUE! | m/s | Speed of sound as a function of pressure and temperature.
w_ph | 1 | bar | 200 | kJ/kg | #VALUE! | m/s | Speed of sound as a function of pressure and enthalpy
w_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | m/s | Speed of sound as a function of pressure and entropy.
Dynamic Viscosity
Viscosity is not part of IAPWS Steam IF97. Equations from "Revised Release on the IAPWS Formulation 1985 for the Viscosity of Ordinary Water Substance", 2003 are used.
Viscosity in the mixed region (4) is interpolated according to the density. This is not true since it will be two fases.
my_pT | 1 | bar | 100 | °C | #VALUE! | Pa s | Viscosity as a function of pressure and temperature.
my_ph | 1 | bar | 100 | kJ/kg | #VALUE! | Pa s | Viscosity as a function of pressure and enthalpy
my_ps | 1 | bar | 1 | kJ/(kg K) | #VALUE! | Pa s | Viscosity as a function of pressure and entropy.
Prandtl
Calcualted as Cp*my/tc
pr_pT | 1 | bar | 200 | °C | #VALUE! | -
pr_ph | 1 | bar | 2875.4751 | kJ/kg | #VALUE! | -
Thermal Conductivity
Revised release on the IAPS Formulation 1985 for the Thermal Conductivity of ordinary water substance (IAPWS 1998)
tcL_p | 100 | bar |  |  | #VALUE! | W/(m K) | Saturated vapour thermal conductivity
tcV_p | 1 | bar |  |  | #VALUE! | W/(m K) | Saturated liquid thermal conductivity
tcL_T | 100 | °C |  |  | #VALUE! | W/(m K) | Saturated vapour thermal conductivity
tcV_T | 100 | °C |  |  | #VALUE! | W/(m K) | Saturated liquid thermal conductivity
tc_pT | 100 | bar | 350 | °C | #VALUE! | W/(m K) | Thermal conductivity as a function of pressure and temperature.
tc_ph | 1 | bar | 350 | kJ/(kg K) | #VALUE! | W/(m K) | Thermal conductivity as a function of pressure and enthalpy
tc_hs | 100 | kJ/(kg K) | 0.34 | kJ/(kg K) | #VALUE! | W/(m K) | Thermal conductivity as a function of enthalpy and entropy
Surface Tension
IAPWS Release on Surface Tension of Ordinary Water Substance, September 1994
st_T | 100 | °C |  |  | #VALUE! | N/m | Surface tension for two phase water/steam as a function of T
st_p | 1 | bar |  |  | #VALUE! | N/m | Surface tension for two phase water/steam as a function of T
Vapour fraction
x_ph | 1 | bar | 1000 | kJ/kg | #VALUE! |  | Vapour fraction as a function of pressure and enthalpy
x_ps | 1 | bar | 4 | kJ/(kg K) | #VALUE! |  | Vapour fraction as a function of pressure and entropy.
Vapour Volume Fraction
Observe that vapour volume fraction is very sensitive. Vapour volume is about 1000 times greater than liquid volume and therfore vapour volume fraction
gets close to the accurancy of steam IF-97
vx_ph | 1 | bar | 418 | kJ/kg | #VALUE! |  | Vapour volume fraction as a function of pressure and enthalpy
vx_ps | 1 | bar | 4 | kJ/(kg K) | #VALUE! |  | Vapour volume fraction as a function of pressure and entropy.
Version history
News in V2.6
* Error in valid region for function tc_ptrho
* Error in function h3_pt for temperatures near the saturation point.
News in V2.5
* DLL distrubution for use in other applications
* Freebasic translation
* Fixed small error in Cv Region 5 p>1000bar
News in V2.4a
* ToSIUnit for h_ps region 4. (No effect in SI unit version).
News in V2.4
* Functions by p,rho inplemented in matlab also.
* Many missing ; in matlab causing printouts detected.
* OpenOffice version introduced. (Fixed calculation differences in open office and excel)
* Matlab error giving varaible undefined in some backwards solutions fixed.
News in V2.3
* Option Explicit, gives more efficient calculations.
* Extensive testing
* my_ph not defined in region 4.
* Problems at region border for h4V_p to adress solver problems at the exact border.
* Problem at fast border check in region_ph fixed.
News in V2.2
* Extensive testing
* Fixed error in Cp_ph
* Function p_hrho added. (Very good for calcualting pressure when heating a volume with water/steam mixture.)
* Fixed error in T_hs return no value for vet region bellow the water saturation line.
* Prandtl number added
News in V2.1
* Calling function h_prho
* Fixed problem with Cv reporting NaN in region 5.
* Equivivalent to the Matlab version. (Downloadable from www.x-eng.com)
News in V2
* Calling functions of h and s added.
* Thermal conductivity, Surface tension added
* Calling functions h_px and h_tx added.
* Cp, Cv and w undefined in the mixed region. (Before interpolation with the vapor fraction was used.)
* A work sheet "Properties" for simple lookups added.